## Slide 1
Maher Attal
On behalf of SESAME team
SESAME Report
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 2
O Introduction
O Machine performance
O Machine upgrades
O Major incidents
O Energy sustainability
Outline
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 3
20MeV Microtron
Ch= 16-24nC, pulse = 2µs
800MeV booster
I = up to 12 mA, pulse = 110 ns
2.5GeV Storge Ring
C =133.2m
εx = 26 nm.rad
Simple DBA lattice, dispersive sections
16 cells & 16 S.S. (8x4.2m + 8x2.2m)
I = 300mA (design value: 400mA)
RF: 500MHz, 1.7MV
x
y
x
80kW, 500MHz SSAs
100kW Elettra cavities
Soft X-ray (70 -1800 eV)
(source: Apple II Undulator)
Tomography (5 -100 keV)
(source: 2.9T 3PW)
Hard X-ray (5 -25 keV)
(source: 1.38T MW)
Hard X-ray (4.7-30 keV)
(source: 1.455T BM)
IR (0.001-3 eV)
(source: BM (includes Edge Radiation))
SESAME Structure
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 4
  Two operator shifts / day: 8:00 – 15:00 and 15:00 – 22:00
  Staff are on call in the period 17:00 – 22:00
  The machine is not attended in the period 22:00 – 8:00
  If the beam is lost after 22:00, recovery will take place next morning
  The machine was running in a “Free Mode” over the weekends
  (recently it is running at injection energy)
Machine Operation Management
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 5
Machine Performance
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 6
  Good beam lifetime, hence one injection / day
Machine Performance

## Slide 7
Chart: Integrated current (A.h)
| 4280 | 4304 | 4327 | 4354 | 4378 | 4414 | 4437 | 4446 | 4471 | 4537 | 4563 | 4594 | 4616 | 4644 | 4661 | 4689 | 4716 | 4749 | 4784 | 4825 | 4841 | 4866 | 4895 | 4921
 | 8859.69 | 8704.197 | 8842.735 | 8806.53 | 8285.97 | 8977.275 | 8728.98 | 8276.52 | 7904.3132 | 8845.16 | 9016.324 | 9130 | 8980.12 | 8756.95 | 9648 | 9350 | 9250 | 8764.6 | 9868.72 | 8785.91 | 8351.481 | 8539.59 | 8241.48 | 8289.5
Beam lifetime in 2025 (Feb – Oct)
250mA
300mA
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 8
Orbit stability and Orbit Feed Back Systems
Beam orbit is corrected by SOFB at 2Hz rate.
Correction rate to be improved to 10Hz
IDs’ orbit distortion is sufficiently compensated
using Feed Forward Tables (FFTs).
No need for FOFB is foreseen at this stage.
RMS in 1-100Hz |  | Horizontal (% of the beam size) |  |  | Vertical (% of beam size) |  | 
 |  | Long Straight | Short Straight | Dipole | Long Straight | Short Straight | Dipole
Beam int. Position (μm) | Tolerance | 82.59 (10%) | 82.08 (10%) | 23.23 (10%) | 2.08 (10%) | 1.42 (10%) | 8.1 (10%)
 | Measured | 9.3 (1.12%) | 9.23 (1.12%) | 5.9(2.54%) | 1.4 (6.73%) | 0.8 (5.63%) | 2.57(3.17%)
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 9
Excluding power grid failure
BA = 98.2 %
MTBF = 185.0 h
MTTR = 1.5 h
Including power grid failure
BA = 97.7 %
MTBF = 122.7 h
MTTR = 1.6 h
Overall Performance
NOTE: machine is not attended in the 3rd shift (22:00-8:00)
Machine Performance in 2025 (until Oct 9)
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 10
Machine Performance in 2025 (until Oct 9)
Chart: Beam Availability (%)
| Run 1 | Run 2 | Run 3 | Run 4
Series1 | 97.2 | 97.5 | 98.2 | 98.3
Series2 | 99.7 | 105.5 | 302.7 | 107.5
MTTR: 1.6h
MTTR: 2.4h
MTTR: 0.8h
MTTR: 0.4h
Beam Availability
MTBF
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025
Performance/ Run

## Slide 11
Chart: Machine downtime (h) Number of failures
| Power Grid | Diagnostic | Network | Control | Cooling | PS | ID | Validation | MotionControl | Microtron | Unknown | RF | Safety | Human Error | Beam Lines
 | 12.75 | 9.15 | 8.7 | 8.05 | 7.5 | 7.25 | 1.4167 | 0.9 | 0.9 | 0.85 | 0.53333 | 0.48333 | 0.31667 | 0.3 | 0.18333
Series 2 | 9 | 2 | 5 | 9 | 13 | 2 | 1 | 2 | 1 | 1 | 3 | 2 | 1 | 2 | 1
Machine downtime & failures in 2025 (until Oct 9)
Machine downtime
Number of failures
21.5%
15.4%
14.7%
13.6%
12.6%
12.2%
2.4%
1.5%
1.5%
1.4%
0.9%
0.8%
0.3%
0.5%
0.5%
Total machine downtime = 59.2 h & Total number of failures = 54
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 12
Chart: Beam Availability (%)
| 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
 | 88.9 | 91.8 | 92.3 | 94.9 | 92.1 | 94.4 | 93.5 | 97.7
 | 17.9 | 35.9 | 25.3 | 69 | 75.9 | 122.7
Beam Availability
MTBF
Exceptional year of power grid instability
Machine Statistics over last years
Including power grid failure
BMS of cooling
system upgraded to PLC (Aug 2024)
Configuration of RF LLEs improved (Sep 2024)
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 13
 | The system’s contribution to machine downtime | 
 | 2024 (Feb – October) | 2025 (Feb – October)
Cooling system | 15.5 h (62% due to BMS) | 6.6 h (0% due to the PLC)
RF system | 79.8 h (88% due to LLE) | 0.5 h
Performance of cooling and RF systems in 2024 versus 2025
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 14
Total shifts: 4392h
=================
User time : 3528h (80.3%)
Machine dev.: 760h (17.3%)
Beamline dev. : 72h (1.64%)
Machine pre. : 32h (0.73%)
Free mode: 56h
Low energy mode: 832h
Machine calendar 2025

## Slide 15
Major Upgrades on the Machine
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 16
Upgrade on compressed air system (Aug 2025)
Two air compressors (ZT15) (31.1 L/s each):
  Running under risky conditions
(exceeded their overhaul time).
  One compressor can’t run the machine
  (machine load ~ 45 L/s).
A single point of failure for the machine
Two new compressors (ZT30) (70.4 L/s each).
The condition “one compressor running, one on standby” is achieved.
The system isn’t critical anymore
Fully funded by PSI
Many thanks
Upgraded to

## Slide 17
A spare power supply for storage ring dipoles
SR dipoles’ PS is a big and complicated system
Any failure takes several days of troubleshooting and repair
A single point of failure for the machine
A spare one has been manufactured by EEI company
Shipment in Nov 2025 & installation in Jan 2026
(The planned fast switching between the two PSs will reduce a lot the MTTR)
Dipole PS
Funded mainly by PSI
Many thanks
Partial fund from SESAME

## Slide 18
Further upgrades on the cooling system soon
Cooling parts donated by SOLEIL arrived at SESAME
Further upgrades on SESAME cooling system are planned starting January 2026
(main SR pumps, heat exchanger, DI water feeding unit, …..)
Many thanks

## Slide 19
The future full energy injector
The draft CDR is finished (under review by the MAC)
Main features:
  A compact 100MeV linac (8.2 – 8.6 m)
  It uses one HG accelerating section (27 – 30 MV/m)
(adopting the design of FERMI HG structure)
  A 30 nm.rad, 118.2 m, 2.5 GeV booster
(attached to the inner of SR tunnel)
  The project is to be done in two phases, keeping
the microtron as a standby pre-injector in phase I.
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 20
The future full energy injector
Why a compact 100MeV linac (8.2 – 8.6m):
  Fits the space available in booster tunnel
  Lower cost (no new bunker is needed)
  Space effective solution
  Less efforts (no construction work required)
  No dark period is needed (installation &
  commissioning can be done during user’s time
  & normal shutdowns)
Phase I:
The linac installed parallel to Microtron with injection
at different section into the 800MeV booster.
The microtron will be kept as a standby pre-injector until reliability of the linac is approved
and good experience is obtained in the new system.
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025
Injection septum
Injection/ extraction kicker

## Slide 21
Phase 1
Phase 2
The future full energy injector
Phase 2
  When the full energy booster
  becomes available.
  Linac to be moved to its final
  location closer to the FEB.
  The 800MeV booster will be dismantled
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025
Injection/extraction section

## Slide 22
Main parameters of the full energy booster
Parameter | Unit | Value
Inj. / ext. energy | GeV | 0.1 / 2.5
C | m | 118.2
Nat. emittance | nm.rad | 30
Qx, Qy |  | 6.77, 4.83
Nat.  x, y |  | -8.52, -11.8
Energy spread | % | 0.1503
Energy loss/turn | keV | 452.7
x, y, s (@100MeV) | s | 27.2, 68.4, 141.3
x, y, s (@2.5GeV) | ms | 1.74, 4.38, 9.05
 | % | 1.521
I max | mA | 10
Repetition rate | Hz | 3
RF frequency | MHz | 500
Harmonic number |  | 197
Peak RF voltage | MV | 0.650
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025
x
y
x

## Slide 23
Major Incidents
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 24
High-voltage cable burned
Incident: A high-power coaxial cable burned in RF SSA1
Date: September, 2024
Reason: A connection loose
Impact:
  4.5h of machine downtime (it was a machine day).
  The burned cable caused partial damage to 6 other
  cables located below it.
Action:
  All damaged cables were replaced.
  Tightness of other cables was verified
  Cable tightness and thermal inspections (thermal camera)
  have been scheduled as part of periodic preventive
  maintenance.

## Slide 25
A strong water leak in the DI water unit
Incident: Strong water leak in DI water unit which sprayed water
on the PLC control panel.
Date: May, 2025
Reason: A crack in the PVC elbow (manufacturing fault ?)
Impact:
  A short circuit in the control panel which disturbed the PLC operation
  Incorrect operation of the SR and RF circuits’ 3-way valves.
Action:
  The PLC panel was dried well and returned to normal operation
  The elbow was replaced temporarily
  (later, it was replaced with stainless steel one)
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 26
High-voltage cable of extraction kicker burned
Incident: Short circuit in the high-voltage coaxial cable of
booster extraction kicker’s PFL.
Date: October, 2025
Reason: Unknow (Insulation problem ?)
Impact: Disabled the extraction kicker & stopped injection
(during the machine time)
Action:
  The cable repaired and its insulation improved
  An industrial high voltage connector to be used
  A scheduled periodic inspection of high-voltage connections
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 27
Failures in Apple II undulator’s motors
Incident: 3 failures in undulator’s motors in 3 years
(gap motor (once) and phase shift motor (twice))
Date: June 2022, Nov. 2024, Oct. 2025
Reason: Unknown (power dip/outage? or radiation?)
Impact: Disabling the undulator’s motion.
Action:
  The motors were replaced
  Temporary lead shielding installed (recently).
  Shielded housings for motors and encoders
  (lead + polyethylene) to be fabricated and
  installed next shutdown.
Gap motor
Phase shift motor
Motor & encoder
shielded with lead sheets
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 28
Energy Sustainability
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025

## Slide 29
SESAME is powered by sun
SESAME became a signatory of the UN Climate Neutral Now initiative
6.5MW Solar Power Plant.
Funded by EU ($ 7.34 M)
Many thanks to EU
Start of operation:
Feb 28, 2019
40km far from SESAME
Supplies SESAME with power through a “Wheeling System”

## Slide 30
Solar power plant (SPP) comparison chart of 2023-2025
Chart: Month
| Jan-23 | Feb-23 | Mar-23 | Apr-23 | May-23 | Jun-23 | Jul-23 | Aug-23 | Sep-23 | Oct-23 | Nov-23 | Dec-23 | Jan-24 | Feb-24 | Mar-24 | Apr-24 | May-24 | Jun-24 | Jul-24 | Aug-24 | Sep-24 | Oct-24 | Nov-24 | Dec-24 | Jan-25 | Feb-25 | Mar-25 | Apr-25 | May-25 | Jun-25
Cost without SPP | 216658.5028 | 348133.1356 | 312399.7175 | 265256.1017 | 324298.3333 | 350676.6667 | 440932.5706 | 151030.1412 | 396148.3898 | 452617.0339 | 414016.9774 | 364145.7345 | 149162.8814 | 419799.096 | 420486.6384 | 280652.5424 | 460465.5367 | 362766.8927 | 502093.7853 | 102301.0452 | 395363.1638 | 464744.8305 | 381548.4463 | 417567.4011 | 164213.6723 | 381116.3842 | 302593.7853 | 358596.5537 | 398350.0282 | 256986.8079
Cost with SPP | 8210.113 | 8610.0565 | 9020.791 | 29156.6949 | 28567.5282 | 32081.6667 | 31968.0508 | 31159.2797 | 30903.8277 | 29503.6441 | 28621.4548 | 27470.7768 | 26047.1045 | 26967.2458 | 27965.0565 | 28466.9209 | 28207.9944 | 32128.9972 | 32068.2627 | 30809.6893 | 31814.1384 | 31141.935 | 30000.4379 | 27601.709 | 26986.6949 | 28402.8531 | 27071.2994 | 27364.4209 | 27770.339 | 31807.8814

## Slide 31
Year | Production (kWh) | Consumption (kWh) | Cost (US$) |  | Savings (US$) | Saved CO2 (Ton)
 |  |  | With SPP | Without SPP |  | 
2019 | 9,541,970 | 7,127,380 | 112,041 | 2,677,801 | 2,565,760 | 6,233
2020 | 9,318,793 | 5,676,520 | 108,182 | 2,132,704 | 2,024,522 | 6,087
2021 | 11,529,373 | 9,726,160 | 137,238 | 3,654,179 | 3,516,941 | 7,531
2022 | 10,812,209 | 8,318,220 | 127,778 | 3,125,207 | 2,997,429 | 7,062
2023 | 10,747,999 | 10,743,270 | 295,274 | 4,036,313 | 3,741,039 | 7,021
2024 | 10,921,502 | 11,596,700 | 353,219 | 4,356,952 | 4,003,733 | 7,134
2025 Jan-Jun | 4,888,385 | 4,955,620 | 169,403 | 1,861,857 | 1,692,454 | 3,193
Total | 67,760,231 | 58,143,870 | 1,303,137 | 21,845,013 | 20,541,877 | 44,260
Electrical energy budget (2019-2025)

## Slide 32
The machine’s energy consumption was getting closer to SPP’s production.
Unplanned requests by Jordan Electric Power Company to stop the SPP
during the weekends in March & April, 2025. Another similar
requests are potential in the future.
Actions taken:
Running the machine at injection energy (low energy mode) during weekends.
Reducing total machine operation time by ~ 14% in 2025 with respect to 2024
(4392h instead of 5088h) (user time reduced by 14% & machine time reduced by 20%)
M. Attal, ESLS33 Meeting, SOLEIL, Oct 29 - 31, 2025
Reducing machine energy consumption

## Slide 33
Machine calendar
2025
Low energy mode
during the weekends
starting May 2025.

## Slide 34
Thank you